## Definitions
NISTR | National Institute of Standards and Technology Interagency Reports
E-W qty | East-West quantity per floor
N-S qty | North-South quantity per floor
Norm Qty | National Institute of Standards and Technology Normative Quantity estimation tool packaged with Federal Emergency Management Agency's Performance Assessment Calculation Tool
SP3 | Seismic Performance Prediction Program by Haselton Baker Risk Group
DS* | Damage State
RC | Repair Class (As defined below)
NA | Not applicable
* DS1, DS2 and DS3 corresponds to damage state 1, 2 and 3 respectively for the component defined by a lognormal distribution
Repair Class Definitions (Source: REDi Guidelines)
Repair Class | Repair Description
3 | Heavily damaged structural or non-structural components which pose a risk to life-safety and must be repaired to achieve Re-occupancy. Consequently, these components must also be repaired to achieve Functional Recovery and Full Recovery, since by definition they follow Re-occupancy
2 | Damaged non-structural components which do not pose a "life-safety" risk or otherwise hinder Re-occupancy but must be repaired to achieve Functional Recovery. Consequently, the competent must all be prepaired to achieve Full Recovery, since by definition it follows Functional Recovery
1 | Minimal or minor cosmetic damage to structural or non-structural components which do not hinder Re-occupancy or Functional Recovery but must be repaired to achieve Full Recovery

## B2-B4
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
NA | Traction elevator —applies to most California installations 1976 or later, most Western States installations 1982 or later and most other U.S. installations 1998 or later | D1014.011 | 24 |  | Each | Norm qty | 0.002 (0.3) rad [RC2] | 0.005 (0.3) rad [RC2] | NA
| Traction elevator—applies to most California installations 1976 or later, most Western States installations 1982 or later and most other U.S. installations 1998 or later | D1014.011_ridr | 24 |  | Each | Norm qty | 0.002 (0.3) rad [RC2] | 0.005 (0.3) rad [RC2] | NA
B4-B2 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 10.58 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 4.76 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| Prefabricated steel stair with steel treads and landings with no seismic joint | C2011.001b | 2 |  | Each | Moehle and others, 2011 | 0.005 (0.6) rad [RC1] | 0.017 (0.6) rad [RC3] | 0.028 (0.45) rad [RC3]

## B1
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
B1 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 10.58 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 4.76 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | D5012.021d | 1 |  | 1,600 A | SP3 | 1.28(0.4)g [RC2] | NA | NA
| Prefabricated steel stair with steel treads and landings with no seismic joint | C2011.001b | 2 |  | Each | Moehle and others, 2011 | 0.005 (0.6) rad [RC1] | 0.017 (0.6) rad [RC3] | 0.028 (0.45) rad [RC3]

## L1
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
L1 | Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only | C3032.001a | 16.83 |  | 250 sq. ft. | SP3 | 1.17 (0.25) g [RC1] | 1.58 (0.25) g [RC3] | 1.82 (0.25) g [RC3]
| Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only | C3032.001b | 7.013 |  | 600 sq. ft. | SP3 | 1.01 (0.25) g [RC1] | 1.45 (0.25) g [RC3] | 1.69 (0.25) g [RC3]
| Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only | C3032.001c | 2.338 |  | 1800 sq. ft. | SP3 | 0.7 (0.25) g [RC1] | 1.2 (0.25) g [RC3] | 1.43 (0.25) g [RC3]
| Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only | C3032.001d | 1.648 |  | 2500 sq. ft. | SP3 | 0.56 (0.25) g [RC1] | 1.08 (0.25) g [RC3] | 1.31 (0.25) g [RC3]
| Independent pendant lighting—nonseismic | C3034.001 | 71 |  | Each | Norm qty | 0.6 (0.4) g [RC3] | NA | NA
| Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY | D2021.021a | 0.21 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC2] | 2.6 (0.4) g [RC3] | NA
| Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | D2021.011a | 0.59 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC2] | 2.6 (0.4) g [RC3] | NA
| Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | D2021.011b | 0.59 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC2] | 2.6 (0.4) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | D2022.011a | 0.02 |  | 1,000 lin ft | SP3 | 0.55 (0.5) g [RC2] | 1.1 (0.5) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | D2022.011b | 0.02 |  | 1,000 lin ft | SP3 | 1.2 (0.5) g [RC3] | 2.4 (0.5) g [RC3] | NA
| Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | D2022.021a | 0.24 |  | 1,000 lin ft | SP3 | 1.5 (0.5) g [RC2] | 2.6 (0.5) g [RC3] | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | D2031.021a | 0.26 |  | 1,000 lin ft | SP3 | 2.25 (0.5) g [RC2] | NA | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | D2031.021b | 0.26 |  | 1,000 lin ft | SP3 | 1.2 (0.5) g [RC3] | 2.4 (0.5) g [RC3] | NA
| HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B | D3041.031a | 4.2 |  | 10 Each | SP3 | 1.3 (0.4) g [RC3] | NA | NA
| HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | D3041.011a | 0.35 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | D3041.012a | 0.09 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 3.74 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 1.683 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| Curtain walls—unitized curtain wall (also generic unitized curtain wall), configuration: symmetric insulating glass units (dual-pane, equal-thick­ness IGU), lamination: not laminated, glass type: full tempered, details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHB™ SGT; glass-frame clearance=0.43 in. (11 mm); aspect ratio=varies; sealant=wet | B2022.201 | 102 | 66 | 30 ft2 | Moehle and others, 2011 | 0.01 (0.3) rad [RC2] | 0.03 (0.3) rad [RC3] | 0.04 (0.3) rad [RC3]
| Wall partition, type: gypsum with metal studs, full height, fixed below, fixed above | C1011.001a | 2.84 | 1.84 | 100 lin ft | Norm qty | 0.005 (0.4) rad [RC1] | 0.01 (0.3) rad [RC1] | 0.021 (0.2) rad [RC2]
| Prefabricated steel stair with steel treads and landings with no seismic joint | C2011.001b | 2 | 1 | Each | Moehle and others, 2011 | 0.005 (0.6) rad [RC1] | 0.017 (0.6) rad [RC3] | 0.028 (0.45) rad [RC3]
| Wall partition, type: gypsum and wallpaper, full height, fixed below, fixed above | C3011.001a | 0.215 | 0.139 | 100 lin ft | Norm qty | 0.0021 (0.6) rad [RC1] | NA | NA
| Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | D5012.021d | 1 |  | 1,600 A | SP3 | 1.28(0.4)g [RC2] | NA | NA

## L2-L40
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
L2-L40 | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY | D2021.021a | 0.84 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC2] | 2.6 (0.4) g [RC3] | NA
| Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | D2021.011a | 2.356 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC2] | 2.6 (0.4) g [RC3] | NA
| Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | D2021.011b | 2.356 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC2] | 2.6 (0.4) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | D2022.011a | 0.09 |  | 1,000 lin ft | SP3 | 0.55 (0.5) g [RC2] | 1.1 (0.5) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | D2022.011b | 0.09 |  | 1,000 lin ft | SP3 | 1.2 (0.5) g [RC3] | 2.4 (0.5) g [RC3] | NA
| Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | D2022.021a | 0.94 |  | 1,000 lin ft | SP3 | 1.5 (0.5) g [RC2] | 2.6 (0.5) g [RC3] | NA
| Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only | C3032.001a | 16.83 |  | 250 sq. ft. | SP3 | 1.17 (0.25) g [RC1] | 1.58 (0.25) g [RC3] | 1.82 (0.25) g [RC3]
| Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only | C3032.001b | 7.013 |  | 600 sq. ft. | SP3 | 1.01 (0.25) g [RC1] | 1.45 (0.25) g [RC3] | 1.69 (0.25) g [RC3]
| Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only | C3032.001c | 2.338 |  | 1800 sq. ft. | SP3 | 0.7 (0.25) g [RC1] | 1.2 (0.25) g [RC3] | 1.43 (0.25) g [RC3]
| Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only | C3032.001d | 1.648 |  | 2500 sq. ft. | SP3 | 0.56 (0.25) g [RC1] | 1.08 (0.25) g [RC3] | 1.31 (0.25) g [RC3]
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | D2031.021a | 1.066 |  | 1,000 lin ft | SP3 | 2.25 (0.5) g [RC2] | NA | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | D2031.021b | 1.066 |  | 1,000 lin ft | SP3 | 1.2 (0.5) g [RC3] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 3.74 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 1.683 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B | D3041.031a | 16.83 |  | 10 Each | SP3 | 1.3 (0.4) g [RC3] | NA | NA
| HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | D3041.011a | 1.403 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | D3041.012a | 0.374 |  | 1,000 lin ft | SP3 | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| Variable Air Volume (VAV) box with in-line coil, SDC A or B | D3041.041a | 3.74 |  | 10 Each | Norm qty | 1.9 (0.4) g [RC2] | NA | NA
| Curtain walls—unitized curtain wall (also generic unitized curtain wall), configuration: symmetric insulating glass units (dual-pane, equal-thick­ness IGU), lamination: not laminated, glass type: full tempered, details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHB™ SGT; glass-frame clearance=0.43 in. (11 mm); aspect ratio=varies; sealant=wet | B2022.201 | 153 | 99 | 30 ft2 | Moehle and others, 2011 | 0.01 (0.3) rad [RC2] | 0.03 (0.3) rad [RC3] | 0.04 (0.3) rad [RC3]
| Wall partition, type: gypsum with metal studs, full height, fixed below, fixed above | C1011.001a | 11.35 | 7.346 | 100 lin ft | Norm qty | 0.005 (0.4) rad [RC1] | 0.01 (0.3) rad [RC1] | 0.021 (0.2) rad [RC2]
| Prefabricated steel stair with steel treads and landings with no seismic joint | C2011.001b | 2 | 1 | Each | Moehle and others, 2011 | 0.005 (0.6) rad [RC1] | 0.017 (0.6) rad [RC3] | 0.028 (0.45) rad [RC3]
| Independent pendant lighting—nonseismic | C3034.001 | 71 |  | Each | Norm qty | 0.6 (0.4) g [RC3] | NA | NA
| Wall partition, type: gypsum and wallpaper, full height, fixed below, fixed above | C3011.001a | 0.858 | 0.555 | 100 lin ft | Norm qty | 0.0021 (0.6) rad [RC1] | NA | NA
| Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | D5012.021d | 1 |  | 1,600 A | SP3 | 1.28(0.4)g [RC2] | NA | NA

## Roof
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
Roof | Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3052.011d | 20 |  | 20,000 ft3/min | SP3 | 0.25 (0.4) g [RC2] | NA | NA
| Chiller - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3031.011d | 3 |  | 250 tons | SP3 | 0.2 (0.4) g [RC2] | NA | NA
| Cooling Tower - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3031.021d | 3 |  | 500 tons | SP3 | 0.5(0.4)g [RC2] | NA | NA