## Definitions
NISTR | National Institute of Standards and Technology Interagency Reports
E-W qty | East-West quantity per floor
N-S qty | North-South quantity per floor
Norm Qty | National Institute of Standards and Technology Normative Quantity estimation tool packaged with Federal Emergency Management Agency's Performance Assessment Calculation Tool
SP3 | Seismic Performance Prediction Program by Haselton Baker Risk Group
DS* | Damage State
RC | Repair Class (As defined below)
NA | Not applicable
* DS1, DS2 and DS3 corresponds to damage state 1, 2 and 3 respectively for the component defined by a lognormal distribution
Repair Class Definitions (Source: REDi Guidelines)
Repair Class | Repair Description
3 | Heavily damaged structural or non-structural components which pose a risk to life-safety and must be repaired to achieve Re-occupancy. Consequently, these components must also be repaired to achieve Functional Recovery and Full Recovery, since by definition they follow Re-occupancy
2 | Damaged non-structural components which do not pose a "life-safety" risk or otherwise hinder Re-occupancy but must be repaired to achieve Functional Recovery. Consequently, the competent must all be prepaired to achieve Full Recovery, since by definition it follows Functional Recovery
1 | Minimal or minor cosmetic damage to structural or non-structural components which do not hinder Re-occupancy or Functional Recovery but must be repaired to achieve Full Recovery

## B2-B4
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
NA | Traction elevator —applies to most California installations 1976 or later, most Western States installations 1982 or later and most other U.S. installations 1998 or later | D1014.011 | 6 |  | Each | Norm qty | 0.002 (0.3) rad [RC2] | 0.005 (0.3) rad [RC2] | NA
| Traction elevator—applies to most California installations 1976 or later, most Western States installations 1982 or later and most other U.S. installations 1998 or later | D1014.011_ridr | 6 |  | Each | Norm qty | 0.002 (0.3) rad [RC2] | 0.005 (0.3) rad [RC2] | NA
B4-B2 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 5.69 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 4.14 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA

## B1
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
B1 | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 5.69 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 4.14 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | D5012.021c | 1 |  | 800 A | SP3 | 1.28(0.4)g [RC2] | NA | NA
| Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | D5012.021d | 2 |  | 1,600 A | SP3 | 1.28(0.4)g [RC2] | NA | NA

## L1
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
L1 | Suspended ceiling, SDC D, E (Ip=1.0), area (A) < 250, vertical and lateral support | C3032.003a | 42 |  | 250 ft2 | Norm qty | 1.6 (0.3) g [RC1] | 1.95 (0.3) g [RC3] | 2.07 (0.3) g [RC3]
| Independent pendant lighting—nonseismic | C3034.001 | 174 |  | Each | Norm qty | 0.6 (0.4) g [RC3] | NA | NA
| Cold-water piping (diam­eter>2.5 in.), SDC D, E, F, PIPING FRAGILITY | D2021.023a | 0.02 |  | 1,000 lin ft | Moehle and others, 2011 | 2.25 (0.4) g [RC1] | 4.1 (0.4) g [RC3] | NA
| Cold-water piping (diam­eter>2.5 in.), SDC D,E,F, BRACING FRAGILITY | D2021.023b | 0.02 |  | 1,000 lin ft | Moehle and others, 2011 | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | D2022.011a | 0.42 |  | 1,000 lin ft | Moehle and others, 2011 | 0.55 (0.5) g [RC1] | 1.1 (0.5) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | D2022.011b | 0.42 |  | 1,000 lin ft | Moehle and others, 2011 | 1.2 (0.5) g [RC3] | NA | NA
| Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | D2022.021a | 0.015 |  | 1,000 lin ft | Moehle and others, 2011 | 1.5 (0.5) g [RC1] | 2.6 (0.5) g [RC3] | NA
| Hot-water piping—large diam­eter welded steel—(diam­eter>2.5 in.), SDC D, E, or F, BRACING FRAGILITY | D2022.023b | 0.015 |  | 1,000 lin ft | Moehle and others, 2011 | 1.5 (0.5) g [RC3] | 2.25 (0.5) g [RC3] | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | D2031.021a | 0.36 |  | 1,000 lin ft | Moehle and others, 2011 | 2.25 (0.5) g [RC1] | NA | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | D2031.021b | 0.36 |  | 1,000 lin ft | Moehle and others, 2011 | 1.2 (0.5) g [RC2] | 2.4 (0.5) g [RC3] | NA
| HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F | D3041.032c | 2.05 |  | 100 Each | Moehle and others, 2011 | 1.5 (0.4) g [RC3] | NA | NA
| HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F | D3041.001c | 0.15 |  | 1,000 lin ft | Norm qty | 2.25 (0.4) g [RC3] | 2.6 (0.4) g [RC3] | NA
| HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | D3041.011a | 0.15 |  | 1,000 lin ft | Norm qty | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 5.69 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 4.14 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| Curtain walls—unitized curtain wall (also generic unitized curtain wall), configuration: symmetric insulating glass units (dual-pane, equal-thick­ness IGU), lamination: not laminated, glass type: full tempered, details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHB™ SGT; glass-frame clearance=0.43 in. (11 mm); aspect ratio=varies; sealant=wet | B2022.201 | 68.9 | 68.9 | 30 ft2 | Moehle and others, 2011 | 0.01 (0.3) rad [RC2] | 0.03 (0.3) rad [RC3] | 0.04 (0.3) rad [RC3]
| Wall partition, type: gypsum with metal studs, full height, fixed below, fixed above | C1011.001a | 1.13 | 1.13 | 100 lin ft | Norm qty | 0.005 (0.4) rad [RC1] | 0.01 (0.3) rad [RC1] | 0.021 (0.2) rad [RC2]
| Prefabricated steel stair with steel treads and landings with no seismic joint | C2011.001b | 2 |  | Each | Moehle and others, 2011 | 0.005 (0.6) rad [RC1] | 0.017 (0.6) rad [RC3] | 0.028 (0.45) rad [RC3]
| Wall partition, type: gypsum and wallpaper, full height, fixed below, fixed above | C3011.001a | 0.59 | 0.59 | 100 lin ft | Norm qty | 0.0021 (0.6) rad [RC1] | NA | NA
| Variable Air Volume (VAV) box with in-line coil, SDC A or B | D3041.041a | 0.15 |  | 10 Each | Norm qty | 1.9 (0.4) g [RC2] | NA | NA

## L2-L42
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
L2–L42 | Cold-water piping (diam­eter>2.5 in.), SDC D, E, F, PIPING FRAGILITY | D2021.023a | 0.08 |  | 1,000 lin ft | Moehle and others, 2011 | 2.25 (0.4) g [RC1] | 4.1 (0.4) g [RC3] | NA
| Cold-water piping (diam­eter>2.5 in.), SDC D,E,F, BRACING FRAGILITY | D2021.023b | 0.08 |  | 1,000 lin ft | Moehle and others, 2011 | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | D2022.011a | 1.66 |  | 1,000 lin ft | Moehle and others, 2011 | 0.55 (0.5) g [RC1] | 1.1 (0.5) g [RC3] | NA
| Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | D2022.011b | 1.66 |  | 1,000 lin ft | Moehle and others, 2011 | 1.2 (0.5) g [RC3] | NA | NA
| Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | D2022.021a | 0.06 |  | 1,000 lin ft | Moehle and others, 2011 | 1.5 (0.5) g [RC1] | 2.6 (0.5) g [RC3] | NA
| Hot-water piping—large diam­eter welded steel—(diam­eter>2.5 in.), SDC D, E, or F, BRACING FRAGILITY | D2022.023b | 0.06 |  | 1,000 lin ft | Moehle and others, 2011 | 1.5 (0.5) g [RC3] | 2.25 (0.5) g [RC3] | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | D2031.021a | 1.43 |  | 1,000 lin ft | Moehle and others, 2011 | 2.25 (0.5) g [RC1] | NA | NA
| Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | D2031.021b | 1.43 |  | 1,000 lin ft | Moehle and others, 2011 | 1.2 (0.5) g [RC2] | 2.4 (0.5) g [RC3] | NA
| HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F | D3041.032c | 8.2 |  | 100 Each | Moehle and others, 2011 | 1.5 (0.4) g [RC3] | NA | NA
| HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F | D3041.001c | 0.6 |  | 1,000 lin ft | Norm qty | 2.25 (0.4) g [RC3] | 2.6 (0.4) g [RC3] | NA
| HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | D3041.011a | 0.58 |  | 1,000 lin ft | Norm qty | 1.5 (0.4) g [RC3] | 2.25 (0.4) g [RC3] | NA
| Variable Air Volume (VAV) box with in-line coil, SDC A or B | D3041.041a | 0.6 |  | 10 Each | Norm qty | 1.9 (0.4) g [RC2] | NA | NA
| Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | D4011.021a | 5.69 |  | 1,000 lin ft | SP3 | 1.1 (0.4) g [RC2] | 2.4 (0.5) g [RC3] | NA
| Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | D4011.031a | 4.14 |  | 100 Each | SP3 | 0.75 (0.4) g [RC2] | 0.95 (0.4) g [RC3] | NA
| Curtain walls—unitized curtain wall (also generic unitized curtain wall), configuration: symmetric insulating glass units (dual-pane, equal-thick­ness IGU), lamination: not laminated, glass type: full tempered, details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHB™ SGT; glass-frame clearance=0.43 in. (11 mm); aspect ratio=varies; sealant=wet | B2022.201 | 68.9 | 68.9 | 30 ft2 | Moehle and others, 2011 | 0.01 (0.3) rad [RC2] | 0.03 (0.3) rad [RC3] | 0.04 (0.3) rad [RC3]
| Wall partition, type: gypsum with metal studs, full height, fixed below, fixed above | C1011.001a-racking | 4.51 | 4.51 | 100 lin ft | Norm qty | 0.005 (0.4) rad [RC1] | 0.01 (0.3) rad [RC1] | 0.021 (0.2) rad [RC2]
| Prefabricated steel stair with steel treads and landings with no seismic joint. | C2011.001b | 2 |  | Each | Moehle and others, 2011 | 0.005 (0.6) rad [RC1] | 0.017 (0.6) rad [RC3] | 0.028 (0.45) rad [RC3]
| Wall partition, type: gypsum and wallpaper, full height, fixed below, fixed above | C3011.001a-racking | 2.38 | 2.38 | 100 lin ft | Norm qty | 0.0021 (0.6) rad [RC1] | NA | NA
| Wall partition, type: gypsum and ceramic tile, full height, fixed below, fixed above | C3011.002a-racking | 3.43 | 3.43 | 100 lin ft | Moehle and others, 2011 | 0.0021 (0.6) rad [RC1] | 0.0071 (0.45) rad [RC1] | NA
| Low voltage switchgear—capacity: 100 to <350 A—equipment is hard anchored—EQUIPMENT FRAGILITY only | D5012.023b | 1 |  | 225 A | Norm qty | 2.4 (0.4) g [RC2] | NA | NA

## Roof
Floor | Component | NISTIR | E-W qty | N-S qty | Units | Source | DS1 median(dispersion)[repair class] | DS2 median(dispersion)[repair class] | DS3 median(dispersion)[repair class]
Roof | Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3052.011b | 1 |  | 8,000 ft3/min | SP3 | 0.25 (0.4) g [RC2] | NA | NA
| Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3052.011c | 2 |  | 20,000 ft3/min | SP3 | 0.25 (0.4) g [RC2] | NA | NA
| Chiller - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3031.011b | 2 |  | 250 tons | Arup estimator | 0.2 (0.4) g [RC2] | NA | NA
| Cooling Tower - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | D3031.021c | 3 |  | 500 tons | SP3 | 0.5(0.4)g [RC2] | NA | NA